## Title
|  |  |  | THIS SECTION IS NORMALLY HIDDEN | DWSPA
|  | Version & Version Date | Version 2.00: November 24, 2011 | <-- Don't edit this; EDIT cells below and watch this change
CLICK LOGO TO HIDE THIS SECTION AGAIN..
Water Supply System |  | Version Date | 2011-11-24 | < UK format date please
Location |  | Version | 2
Approval Holder |  | Default zoom | 100
Approval Number |  | Menu Page name | Menu
AbWARN |  | RegisterPage | Register
DWSP Author |  | Date Format (for Act.Summ Pg) | mmm dd, yyyy | < please me careful here
|  |  | Risk Page Column Widths | Act. Summ Col Widths
|  |  | 30 | 30
|  |  | 30 | 30
| Version 2.00: November 24, 2011 |  | 10 | 13
|  |  | 18 | 30
|  |  | 30 | 30
|  |  | 30 | 11
|  |  | 21 | 12
|  |  | 27 | 14
|  |  | 25 | 14
|  |  | 22 | 25
12
14
9
9
9
9
27
14
M
R

## KEY
KEY / Instruction Page
Buttons and their actions
|  | Jump to Register Page | Reformats all rows on a risk page (replaces eqns, cond. Formatting and drop downs)
|  | Jump to Menu Page | Inserts row above cursor position (then formats it and offers risk type)
Toggles screen Split on and off
Go to previous group page
Go to next group page
M
R
S
<
>
REFORMAT ALL
INS

## Register
SHEET REGISTER
CLICK SHEET NAMES TO NAVIGATE
(This page refreshes each time it is activated)
Sheet Name | #REF!
Title
KEY
DWSP Intro
Glossary
Sheet Guide
Menu
Risk Scoring
Core Detail
Source Detail
Source Schematic
Source Risks
Treatment Detail
Treatment Schematic
Treatment Risks
Network Detail
Network Schematic
Network Risks
Customer Detail
Customer Risks
Key Risks
Action Summary
SOPs

## DWSP Intro
Approval Holder
Water Supply System
Approval Number
Location
About Drinking Water Safety Plans
A Drinking Water Safety Plan is a systematic method of risk management that may be applied to any water supply system. It is based on the analysis of detailed knowledge of the whole water supply system from source to tap and its fundamental purpose is to ensure the safety of the supply at all times. It considers four main areas of supply: source, treatment, distribution network and customer. The risks attached to each section are analysed using a combination of likelihood and consequence and the most significant risks must then be assigned an appropriate mitigation. The plan records all of this information in various forms and is updated on a regular basis. It is a 'living document' that provides the operator with an efficient means of managing risk and is a useful single source of information about the supply.
About this template
This template has been designed to enable you to systematically record the main details of your water supply system and to assess the potential risks to public health. It is divided into four main sections, source, treatment, network and customer and you will be expected to supply the main details, a schematic and then to assess the risks for each section. The amount of detail required will depend on the nature and complexity of your system. You have been provided with a list of common water supply risks to help you, but it is very important that you also think about any specific risks that might be present in your own system. A guide on how the risks are assessed is given in the risk scoring sheet. Once the major risks are identified they must be carried forward to the Major Risks sheet, where you need to consider the most appropriate way of diminishing each risk. You will obviously be constrained by resources and you may need to think about short-term ways of mitigating the risk before you can put in place a permanent solution. Once you have completed this section you then need to record all of the actions that you have identified into the Action Summary sheet. A brief guide to the function of each of the sheets is given in the Sheet Guide
M

## Glossary
Approval Holder
Water Supply System
Approval Number
Location
Glossary of commonly used terms and Abreviations
Term | Definition
AbWARN | The mission of the Alberta Water/Wastewater Agency Response Network (AbWARN) is to support and promote a province-wide emergency preparedness, disaster response, and mutual assistance program for public and private water and wastewater utilities.
Anatoxins | A group of algal neurotoxins produced by the Anabaena species of blue-green algae.
Breakthrough | The situation where barrier filtration is no longer effective and material starts to pass through the filter.
Cause | The action, situation or state that has led to a particular effect or event.
CIP | Cleansing in place. Applies to cleaning of membranes, usually with citric acid
Consequence | The assessed outcome of any hazardous event
Control Measure | Any action or activity that is used to prevent or eliminate a water safety hazard or reduce the risk of it occurring to an acceptable level.
Contingency Plan | A plan of action that will be operated should a hazard or group of hazards enter the distribution system creating a situation where there is an acute risk to Public Health.
Cryptosporidium | A protozoan parasite common in water that causes a severe diarrhoeal disease, cryptosporidiosis. As part of its lifecycle it forms a cyst (oocyst) that is very resistant to normal means of disinfection. It is, however, deactivated by exposure to UV light and will be removed by barrier filtration.
Cyanotoxins | A large group of organic compounds released by the breakdown of blue green algal cells. Amongst other effects they may cause neurological damage, liver damage, or cause diarrhoea.
DWSP | Drinking Water Safety Plan
Event | An incident or situation resulting in an increased public health risk in the water supply.
Geosmin | An organic compound produced by blue-green algae that causes and earthy/musty taste and odour problem in water.
Giardia | A protozoan parasite common in water that causes a severe diarrhoeal disease, giardiasis. As part of its lifecycle it forms a cyst that is very resistant to normal means of disinfection. It is, however, deactivated by exposure to UV light and will be removed by barrier filtration.
Hazard | A chemical, biological, physical or radiological presence with a potential adverse human health effect.
HACCP | Hazard Analysis and Critical Control Point
Likelihood | Probability that an event will happen.
MAC | Maximum Acceptable Concentration.
MIB | 2'Methylisoborneol. An organic compound produced by blue-green algae that causes an earthy/musty taste and odour problem in water.
Microbiological Contamination | Results from the presence of pathogenic bacteria or protozoans. The presence of pathogenic bacteria (e.g E.Coli) often results from a fault with disinfection, but in the case of protozoans, for example Cryptosporidium or Giardia from the failure or lack of barrier filtration.
Microcystins | A group of toxins produced by blue green algae, specifically Microcystis, that cause liver damage.
Pathogenic | Capable of causing disease, in DWSPs specifically to humans.
Protozoan | Any of a large group of single celled organisms, usually too small to be seen with the naked eye, and characterised by their ability to move. They often include a resistant cyst form as part of their lifecycle, and some species such as Cryptosporidium and Giardia are responsible for a lot of waterborne disease.
PRV | Pressure reducing valve
OSEC | On-site electrolytic chlorination
Risk | The probability of something happening that will impact on water safety. It is measured in terms of likelihood and consequence.
Risk Score | A numerical expression of risk derived from the product of likelihood and consequence.
Schematic | A schematic (diagram) represents the elements of a system using abstract, graphic symbols rather than realistic pictures and is not drawn to scale.
Validation | Confirmation that a process fulfils its intended function
Verification | Confirmation that the stated data or processes are correct.
WHO | World Health Organisation.
WTW | Water Treatment Works
M

## Sheet Guide
Approval Holder
Water Supply System
Approval Number
Location
Explanation of sheets included in template & their function
Sheet Name | Purpose | Details
Title | Identifies Site | Water supply name, owner, site manager, WSP author, date of completion, next planned review date
DWSP Intro | Information | Provides summary of DWSP process and how the DWSP is put together
Glossary | Information | Provides a definition for commonly used terms and abbreviations
Sheet Guide | Information | Guide to the purpose & detail of each component sheet
Menu | Quick links to other areas of plan | Simple structure showing main areas with hyperlinks to start of each section
Risk Scoring | Information | Example of matrix and how risk scores are derived
Core Detail | Site Information | Main details of the system, people involved in the making of the plan and main stakeholders
Source Detail | Information | Main details of the watershed, reliable yield, watershed type, watershed activities, etc., and any raw water mains
Source Schematic | Information | Schematic showing the source to the point of treatment, using standard symbols.
Source Risks | Risk assessment | Pre-populated with standard risks with consequence pre-scored. Additional site specific risks to be added as required. Each line must be reviewed to see if it applies at this site and all of the other detail added.
Treatment Detail | Information | Full account of the treatment process including constituent parts, chemicals used etc
Treatment Schematic | Information | Schematic showing full treatment process including any on-line monitoring, using standard symbols
Treatment Risks | Risk assessment | Pre-populated with standard risks with consequence pre-scored. Additional site specific risks to be added as required. Each line must be reviewed to see if it applies at this site and all of the other detail added.
Network Detail | Information | Main details of the distribution network including any pump stations, service reservoirs, and length and type of mains
Network Schematic | Information | Schematic showing the distribution network, using standard symbols.
Network Risks | Risk assessment | Pre-populated with standard risks with consequence pre-scored. Additional site specific risks to be added as required. Each line must be reviewed to see if it applies at this site and all of the other detail added.
Customer Detail | Information | Details of numbers of properties domestic/commercial, key customers/at risk customers, etc.
Customer Risks | Risk assessment | Pre-populated with standard risks with consequence pre-scored. Additional site specific risks to be added as required. Each line must be reviewed to see if it applies at this site and all of the other detail added.
Key Risks | Risk assessment | Summary of risks that exceed an agreed acceptable level and what actions are required to mitigate the risks.
Action Summary | Risk Mitigation | Details of how the unacceptable risks are to be mitigated, by whom, when and funding
SOPs | Information | Summary of standard operating procedures, relating to this water supply system.
M

## Menu
Approval Holder
Water Supply System
Approval Number
Location
Menu Page
This page contains shortcuts around the spreadsheet and will take you either to the start of a section or to another commonly used sheet. Simply click on the box description that you want and it will transfer you to that sheet
Main areas
Source | Treatment | Network | Customer
Other useful links
DWSP Intro | Core Detail | Key Risks | Action Summary
R

## Risk Scoring
Approval Holder
Water Supply System
Approval Number
Location
Risk Scoring Guide
This page explains the rationale behind risk scoring. It provides an explanation of the numbers used for likelihood and consequence and a matrix indicates the level of derived risk (risk score), and the level of threat that each represents. It should be noted that although the risk score gives an indication of the level of risk posed it is a semi-quantitative guide value only and not an absolute number.
Likelihood
The likelihood is a measure of the frequency with which any event is likely to occur. Six levels of likelihood are used and their definitions are shown below. to describe the assessed frequency and a nominal value is attached to each.
Likelihood Table
Likelihood | Definition | Value
Not applicable | Does not apply in this water supply system | 0
Most Unlikely | Conceivable but extremely small chance of happening in next 4-5 years | 1
Unlikely | Is possible and cannot be ruled out in next 4-5 years. | 2
Medium | As likely as not to happen in next 4-5 years. | 4
Probable | Would be expected to happen in next 4-5 years but there is a small chance it may not. | 8
Almost Certain | Would be confident this will happen at least once in next 4-5 years | 16
Consequence
The consequence is a measure of the severity of the event which is likely to occur. Six levels of consequence are used and their definitions shown below. to describe the assessed frequency and a nominal value is attached to each.
Consequence Table
Consequence | Definition | Value
Not applicable | Does not apply in this water supply system | 0
Insignificant | Wholesome water or interruption < 8 hrs | 1
Minor | Short term or localised non-compliance, non health related e.g. aesthetic or interruption 8-12 hrs | 2
Moderate | Widespread aesthetic issues or long term non compliance, not health related or interruption 12-24 hrs | 4
Severe | Potential Illness or interruption >24 - 48 hrs | 8
Catastrophic | Actual illness or potential long term health effects or interruption >48 hrs | 16
|  |  | Risk Matrix |  |  | Consequence Descriptor
|  |  |  | Score | Not Applicable | Insignificant | Minor | Moderate | Severe | Catastrophic
|  |  |  | Not Applicable | 0 | 1 | 2 | 4 | 8 | 16
|  |  | Consequence Descriptor | Most Unlikely | 1 | 1 | 2 | 4 | 8 | 16
|  |  |  | Unlikely | 2 | 2 | 4 | 8 | 16 | 32
|  |  |  | Medium | 4 | 4 | 8 | 16 | 32 | 64
|  |  |  | Probable | 8 | 8 | 16 | 32 | 64 | 128
|  |  |  | Almost Certain | 16 | 16 | 32 | 64 | 128 | 256
Note: The score of "0" should only be applied if the risk is not applicable in this water supply system.
M

## Core Detail
Approval Holder
Water Supply System
Approval Number
Location
Basic Details
Municipal Authority
Approval Number
Water Supply System
Main Contact/Operator
Source
Source Type
Watershed Area
Reliable Yield
Diversion Licence
Main hazards
Treatment
Main Process
Design Capacity
Average Throughput
Storage
Network
Network Length
Network Materials
Network Storage
Domestic Properties (No.)
Business Properties (No.)
Customer
Bylaws in Operation
Hospitals
Home Dialysis Patients
Prisons etc.
Other Vulnerable Customers
Significant Manufacturers
M

## Source Detail
Approval Holder | Source types
Water Supply System | Well
Approval Number | Spring
Location | Drilled Well
Lake
Source Information
Water Supply System
Source Type
Source Description
Watershed Area
Diversion Licence
Yield
Inlet or pump arrangements
Raw Water Mains (length, diameter, condition)
Activities within watershed
Agricultural Discharges/Run-off (manure, etc.)
Municipal Discharges/Run-off (raw or treated wastewater, stormwater, etc.)
Discharges from septic fields/tanks or other non-municipal unsewered human activity
Industrial Discharges/Run-off
Recerational Discharges/Run-off
Comments
M
>
<

## Source Schematic
Approval Holder
Water Supply System
Approval Number
Location
(Insert Schematic)
M
>
<

## Source Risks
Approval Holder
Water Supply System
Approval Number
Location
Note: Shallow wells from river gravels should be regarded as surface water as much of the recharge may be coming from the adjacent watercourse
| Risk Description | Risk I.D. | Hazard | Cause of Potential Failure | Comments | Current Monitoring | How Risk is Currently Controlled | Assess if Control is Adequate | Do any Standard Procedures cover this | Likelihood | Consequence | L'Hood Score | Cons. Score | Risk Score | Key Risk? | Required Interventions to Prevent Failure | Responsible Party
General Risks | Microbiological contamination of raw water as a result no restriction in access to source | DWSP-S-001 | Microbiological contamination | Due to livestock having access to source due to inadequate fencing. | [9 empty] | 0 | No
General Risks | Microbiological contamination of raw water resulting from wildlife activity in watershed. | DWSP-S-002 | Microbiological contamination | Due to wildlife dying or defecating in watershed. | Some animals such as beaver can carry Giardia and other pathogenic organisms | [8 empty] | 0 | No
General Risks | Deterioration of water quality due to birds roosting on reservoirs at night | DWSP-S-003 | Microbiological contamination | Due to bird roost due to large faecal loading | Bird excrement contains very large numbers of bacteria. | [8 empty] | 0 | No
General Risks | Contamination of raw water with sewage | DWSP-S-004 | Microbiological contamination | Resulting from sewage input to the source from private septic tanks or sewer outfalls. | [9 empty] | 0 | No
General Risks | Chemical contamination of raw water as a result of proximity to transport corridor. | DWSP-S-005 | Chemical contamination Hydrocarbons | Due to chemical contamination in the source due to spillage from transport corridor (e.g. road or rail tanker) adjacent to source and no containment. | May result from accidental spillage or a crash. | [8 empty] | 0 | No
General Risks | Chemical contamination of raw water as a result proximity to airport or disused airport | DWSP-S-006 | Chemical contamination Hydrocarbons | Due to chemical contamination in the source due to spillage from airport adjacent to source and no containment. | May result from accidental spillage or a crash. May also be due to use of chemicals within airport as result of uncontrolled run-off e.g. de-icing fluid. | [8 empty] | 0 | No
General Risks | Chemical contamination of raw water as a result of mining activity | DWSP-S-007 | Heavy metals Hydrocarbons | Due to uncontained spillage or disturbed ground within watershed. | [9 empty] | 0 | No
General Risks | Chemical contamination of raw water as a result of mining activity drainage | DWSP-S-008 | Heavy metals Hydrocarbons | Due to mine drainage discharge being contaminated or deoxygenated | [9 empty] | 0 | No
General Risks | Chemical contamination of raw water as a result of recreational activity within watershed | DWSP-S-009 | Microbiological contamination Hydrocarbons | Due to uncontrolled defecation or use of land or water vehicles within watershed | [9 empty] | 0 | No
General Risks | Contamination of water with nutrients, due to agricultural activity. | DWSP-S-010 | Algal bloom Reduced oxygen level in water. | Due to contamination in run-off from areas of agricultural activity. | There are a number of different sources: silage pits, sludge lagoons, concentrations of stock. | [8 empty] | 0 | No
General Risks | Contamination of water with pathogens due to agricultural activity. | DWSP-S-011 | Microbiological contamination | Due to contamination in run-off from areas of agricultural activity. | [9 empty] | 0 | No
General Risks | Contamination of raw water with pesticides | DWSP-S-012 | Pesticides | Resulting from pesticides spraying in the watershed due to poor practice. | [9 empty] | 0 | No
General Risks | Deterioration of raw water as a result of flooding or heavy rain | DWSP-S-013 | Turbidity | Due to inability to close intake when raw water has deteriorated. | Lack of storage may also influence ability to close intake; high sediment loading resulting from high level of rainfall or spring melt. | [8 empty] | 0 | No
General Risks | Deterioration of raw water from forestry activities | DWSP-S-014 | Turbidity Colour Iron & manganese | Resulting from poor quality surface run-off from forestry activities due to forestry within watershed. | When brush and vegetation are removed the rate of erosion will often increase transporting solids to the watercourse. | [8 empty] | 0 | No
General Risks | Contamination of raw water from forestry activities | DWSP-S-015 | Fertilizers Hydrocarbons Microbiological contamination | As a result of forestry-related human activity within watershed. | Many forestry activities will result in chemicals being brought into watershed. Human waste may also produce pathogenic organisms. | [8 empty] | 0 | No
General Risks | Contamination of raw water as a result forestry fires | DWSP-S-016 | Chemical contamination | Due to change in soil chemistry as a result of heat or run-off rate as a result of reduced vegetation | [9 empty] | 0 | No
General Risks | Contamination as a result of waste disposal site within watershed. | DWSP-S-017 | Hydrocarbons Heavy metals Organics | As a result of leachate from waste disposal site getting into watercourse | [9 empty] | 0 | No
General Risks | Contamination as a result of disposal of animal remains within watershed | DWSP-S-018 | Microbiological contamination | As a result of leachate from the disposal site getting into watercourse | [9 empty] | 0 | No
General Risks | Changing raw water quality caused by environmental change | DWSP-S-019 | Manganese | Due to increase in manganese level resulting from changing weather patterns. | Increased temperature or inversion in lakes may cause manganese release. | [8 empty] | 0 | No
General Risks | Deterioration of raw water quality caused by shallow water body and wind effects | DWSP-S-020 | Turbidity Colour Manganese | Resulting from shallow water body and wind induced turbulence. | Storm conditions may stir up sediment and make treatment more difficult. | [8 empty] | 0 | No
General Risks | Contamination of raw water resulting from algal blooms | DWSP-S-021 | Algae | Due to algal blooms due to increased nutrient levels or changing weather patterns. | Algal cells may clog filters causing poor quality or lower throughput. Blue green algae produce toxins. | [8 empty] | 0 | No
General Risks | Insufficient raw water quantity | DWSP-S-022 | Loss of supply | Resulting from restriction in diversion licence due to changing legislation or growth in demand. | Changes in environmental legislation may lead to tighter diversion limits. | [8 empty] | 0 | No
[14 empty] | 0 | No
General Risks | Insufficient water available for abstraction | DWSP-S-023 | Low pressure Loss of supply | As a result of drought. | [9 empty] | 0 | No
Well Risks | Contamination of well during construction | DWSP-S-024 | Microbiological contamination Metals Drilling fluids | Cross-contamination by drilling equipment or residual substances used in drilling e.g. Barium released from drilling mud. | Drillers should operate according to the Water (Ministerial) Regulations | [8 empty] | 0 | No
Well Risks | Contaminated water entering well from upper levels | DWSP-S-025 | Microbiological contamination Nutrients | Well casing does not extend above surface or is damaged or deteriorated. | Water at upper levels of well more prone to surface effects. Downhole camera inspection | [8 empty] | 0 | No
Well Risks | Contaminated water entering well from surface | DWSP-S-026 | Microbiological contamination Nutrients | Well head badly constructed, damaged, or badly maintained. | Well head should be inspected and assessed for risk. | [8 empty] | 0 | No
Well Risks | Contaminated water entering well from surface | DWSP-S-027 | Microbiological contamination Nutrients | Site prone to flooding due to poor siting and well head not sealed. | Well head should be inspected and assessed for risk. | [8 empty] | 0 | No
Well Risks | Contaminated water entering well from surface | DWSP-S-028 | Microbiological contamination Nutrients | Inadequate security around well head giving animals access. | Well head should be inspected and assessed for risk. | [8 empty] | 0 | No
Well Risks | Deterioration of water quality | DWSP-S-029 | Iron manganese | Due to over-production from aquifer, mixing with other zones or biofouling | Well should not be pumped higher than recommended rate, downhole camera inspection, shock chlorination, rehabilitation | [8 empty] | 0 | No
Well Risks | Deterioration of water quality | DWSP-S-030 | Fluoride Arsenic Uranium Other heavy metals | Due to naturally occurring minerals | [9 empty] | 0 | No
Well Risks | Contamination of aquifer | DWSP-S-031 | Hydrocarbons Pesticides Nutrients | Activities within recharge zone or vulnerable aquifer | More likely with shallow wells, unconfined aquifers or where rock is badly faulted or fractured. | [8 empty] | 0 | No
Springs Risks | Contamination of spring at collection chamber | DWSP-S-032 | Microbiological contamination Suspended solids | As a result collection chamber design or poor maintenance. | Structure should be well maintained. | [8 empty] | 0 | No
Springs Risks | Contamination of spring at collection chamber | DWSP-S-033 | Microbiological contamination Suspended solids | As a result of inadequate security round collection chamber and animal or human activity. | The rock around springs is often fractured so an adequately fenced protection zone is desirable. | [8 empty] | 0 | No
Springs Risks | Contamination of aquifer | DWSP-S-034 | Chemical contamination Microbiological contamination | As a result of human/animal activities in the recharge zone | If the recharge zone is small it may be possible to prevent some activities if shown to be adverse. | [8 empty] | 0 | No
Pumps & Mains Risks | Reduced resource availability due to break/leak on raw water mains | DWSP-S-035 | Loss of supply | Resulting from raw water main breaks/leaks as a result of poor mains condition. | Lack of maintenance may lead to more frequent interruptions to supply. | [8 empty] | 0 | No
Pumps & Mains Risks | Contamination due to insecure break-pressure tank. | DWSP-S-036 | Microbiological contamination | As a result of contamination entering break-pressure tank. | Break-pressure tanks are often poorly maintained | [8 empty] | 0 | No
Pumps & Mains Risks | Failure of pumps at Pump Station | DWSP-S-037 | Loss of supply | Resulting from pumps failure due to insufficient/no standby generation if electricity supply fails. | [9 empty] | 0 | No
Pumps & Mains Risks | Loss of power to pumps as a result of electrical fault. | DWSP-S-038 | Loss of capacity | Loss of power to pumps due to control panel fault resulting from insufficient maintenance. | Essential components need to be maintained regularly. | [8 empty] | 0 | No
Facility Specific Risks |  | DWSP-S-100 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-S-101 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-S-102 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-S-103 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-S-104 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-S-105 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-S-106 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-S-107 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-S-108 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-S-109 | [11 empty] | 0 | No
S
M
>
<
REFORMAT ALL
INS

## Treatment Detail
Approval Holder
Water Supply System
Approval Number
Location
Treatment Information
Water Supply System
Treatment Type
Treatment Description
Primary Treatment
Secondary Treatment
CT
Design Capacity
Chemicals Used in Process
On-line monitors
Treated Water Storage
Stand-by Generator
Sludge Treatment Process
Comments
Note on D11: home: May be useful to put in drop down list and define treatment types.Need to list and agree
M
>
<

## Treatment Schematic
Approval Holder
Water Supply System
Approval Number
Location
(Insert Schematic)
M
>
<

## Treatment Risks
Approval Holder
Water Supply System
Approval Number
Location
| Risk Description | Risk I.D. | Hazard | Cause of Potential Failure | Comment | Current Monitoring | How Risk is Currently Controlled | Assess if Control is Adequate | Do any Standard Procedures cover this | Likelihood | Consequence | L'Hood Score | Cons. Score | Risk Score | Key Risk | Required Interventions to Prevent Failure | Responsible Party
Pre-treatment Risks | Inability to meet demand as a result of failure of cartridge filters | DWSP-T-001 | Loss of Supply | Due to blocking due to deterioration of raw water quality. | [9 empty] | 0 | No
Pre-treatment Risks | Inability to meet demand as a result of failure of microstrainers | DWSP-T-002 | Loss of Supply | As a result microstrainers blocking due to failure of microstrainer wash pump to wash screens adequately. | [9 empty] | 0 | No
Pre-treatment Risks | Inadequate treatment due to poor contact chamber design | DWSP-T-003 | Turbidity Microbiological contamination | Inefficient filtration due to incorrect contact time for coagulant. | [9 empty] | 0 | No
Pre-treatment Risks | Loss of supply caused by failure of heating at works inlet | DWSP-T-004 | Loss of Supply | As a result of mechanical failure due to poor maintenance | [9 empty] | 0 | No
Pre-treatment Risks | Loss of supply caused by failure of inlet control valve | DWSP-T-005 | Loss of Supply | As a result of frozen inlet due to low temperatures and no heating | [9 empty] | 0 | No
General Risks | Breakthrough of algal breakdown products as a result of failure of carbon dosing | DWSP-T-006 | Taste & odour Algal toxins | Due to failure to remove algal by-products in the water due to lack of carbon dosing | Geosmin and MIB impart a strong earthy musty taste to water. Algal toxins are pathogenic. | [8 empty] | 0 | No
General Risks | Breakthrough of contaminants as a result of poor floc formation caused by incorrect or no dosing | DWSP-T-007 | Turbidity Aluminium Iron Microbiological contamination | due to poor floc formation due to incorrect coagulant dose due to flow meter out of calibration or signal failure due to inadequate maintenance | [9 empty] | 0 | No
General Risks | Contamination caused by unauthorised human access | DWSP-T-008 | Unknown contamination | Unauthorised human access may lead to contamination. | WTWs should be kept secure at all times when not attended. | [8 empty] | 0 | No
General Risks | Contamination of treated water as a result of dosing with incorrect or inferior quality chemicals | DWSP-T-009 | Chemical contamination | Contamination due to use of incorrect or inferior quality or contaminated chemicals due to lack of control check on deliveries. | Might be due to change in supplier or inadequate specification for chemicals used. | [8 empty] | 0 | No
General Risks | Deterioration of treated water quality as a result of failure of coagulant dosing | DWSP-T-010 | Trace organics Turbidity Iron Manganese | As a result of failure to dose coagulant due to dosing line blocked. | [9 empty] | 0 | No
General Risks | Deterioration of treated water quality as a result of incorrect or no permanganate dosing | DWSP-T-011 | Taste and odour Colour | Due to not setting the dose at the right level or failure of dosing system | [9 empty] | 0 | No
General Risks | Inability to meet demand as result of damage to single line interprocess pipework | DWSP-T-012 | Loss of Supply | Structural failure due to failure of single line interprocess pipe work; i.e. Interruption to process. | General issue common to most WTWs | [8 empty] | 0 | No
General Risks | Inability to meet demand caused by power failure | DWSP-T-013 | Loss of Supply | Resulting from power failure and to failure of stand by generator change over or no standby generator. | Many small WTW will have no standby power generation | [8 empty] | 0 | No
General Risks | Inadequate treatment as a result of raw water bypassing all or part of the treatment process | DWSP-T-014 | Chemical contamination Microbiological contamination | As a result of no treatment to the raw water | Ideally treatment bypasses should not exist. Where they do they should be secured and signed. | [8 empty] | 0 | No
General Risks | Inadequate pH adjustment as a result of break in dosing pipework | DWSP-T-015 | pH | Due to flooding of dosing pump due to break of make up water piping in dosing room and inadequate drainage. | [9 empty] | 0 | No
General Risks | Inadequate treatment as a result of failure to reach optimum coagulation pH. | DWSP-T-016 | Aluminium Iron | Failure of optimum coagulation due to over-or under dosing of pH adjustment due to mechanical failure | Duty/stand-by system of operation would normally control this. | [8 empty] | 0 | No
General Risks | Inadequate treatment caused by incorrect dosing of chemicals | DWSP-T-017 | Chemical contamination | Due to incorrect dosing due to faulty equipment. | [9 empty] | 0 | No
General Risks | Loss of supply as a result of flooding | DWSP-T-020 | Loss of Supply | Due to plant shut down as a result of flooded areas of plant. | [9 empty] | 0 | No
General Risks | Contamination due to incorrectly plumbed drains | DWSP-T-021 | Chemical contamination Microbiological contamination | Due to inappropriate cross-connection of drainage into treated water areas. | [9 empty] | 0 | No
General Risks | Contamination or loss of supply due to lack of knowledge of infrastructure location | DWSP-T-022 | Chemical contamination Microbiological contamination | Due to lack of adequate 'as-built' drawings | [9 empty] | 0 | No
Process Control Risks | Loss of supply resulting from failure of telemetry. | DWSP-T-018 | Loss of supply | Due to plant shut down not being notified due to failure of telemetry | [9 empty] | 0 | No
Process Control Risks | Loss of supply resulting from failure of the control system | DWSP-T-019 | Loss of supply | Due to inability to run the plant as a result of PLC software failure or to voltage variation and lack of power surge protection. | If control system fails the plant may not be able to run on manual. | [8 empty] | 0 | No
Sedimentation Risks | Inadequate treatment as a result of unstable sludge blanket | DWSP-T-023 | Turbidity Aluminium Iron Microbiological contamination | As a result of increased loading on secondary filters due to carry-over of floc from sedimentation stage. | [9 empty] | 0 | No
Sedimentation Risks | Inadequate treatment as a result of insufficient de-sludging | DWSP-T-024 | Turbidity Aluminium Iron Microbiological contamination | As a result of increased loading on secondary filters due to carry over of floc from sedimentation stage. | [9 empty] | 0 | No
Sedimentation Risks | Inadequate treatment as a results of temperature variation in incoming water upsetting settlement | DWSP-T-025 | Turbidity Aluminium Iron Microbiological contamination | Due to warmer water upsetting settlement due to changes in raw water temperature. | [9 empty] | 0 | No
DAF Risks | Inadequate treatment as a result of insufficient air saturation | DWSP-T-026 | Turbidity Aluminium Iron Microbiological contamination | Due to insufficient flotation as a result of insufficient air saturation. | [9 empty] | 0 | No
DAF Risks | Inadequate treatment as a result of insufficient de-sludging | DWSP-T-027 | Turbidity Aluminium Iron Microbiological contamination | As a result of increased load due to sludge carry over to filters | Important to set the desludge at the right interval. | [8 empty] | 0 | No
DAF Risks | Inadequate treatment as a result of unstable float | DWSP-T-028 | Turbidity Aluminium Iron Microbiological contamination | As a result of increased load due to sludge carry over to filters | [9 empty] | 0 | No
DAF Risks | Inadequate treatment as a result of failure of air blowers | DWSP-T-029 | Turbidity Aluminium Iron Microbiological contamination | As a result of failure of flotation. | [9 empty] | 0 | No
DAF Risks | Inadequate treatment as a result of failure of floating sludge removal mechanism | DWSP-T-030 | Turbidity Aluminium Iron Microbiological contamination | As a result of no sludge removal | [9 empty] | 0 | No
Washwater Risks | Contamination of raw water or water in treatment with wash water / sludge supernatant | DWSP-T-031 | Turbidity Chemical contamination Microbiological contamination | As a result of carry-over in recycled washwater. | [9 empty] | 0 | No
Washwater Risks | Contamination of recovered wastewater in inlet works caused by chemical spill entering wastewater system | DWSP-T-032 | Chemical contamination | Due to uncontrolled spillage due to washwater recycling | [9 empty] | 0 | No
Washwater Risks | Contamination of water due anaerobic conditions in washwater treatment process. | DWSP-T-033 | Chemical contamination Taste and odour | Due to formation of phenolic compounds due to breakdown of sludge due to anaerobic activity | [9 empty] | 0 | No
Washwater Risks | Restriction of supply due to problems with washwater storage capacity | DWSP-T-034 | Loss of Supply | As a result of restriction in filter wash frequency due to mechanical breakdown or high loading on filters. | [9 empty] | 0 | No
Washwater Risks | Restriction of supply due to problems with sludge de-watering/disposal capacity | DWSP-T-035 | Loss of Supply | As a result of inadequate capacity to de-water sludge as a result of difficult conditions or significant increase in sludge produced. | [9 empty] | 0 | No
Washwater Risks | Restriction of supply due to problems with sludge disposal capacity | DWSP-T-036 | Loss of Supply | As a result of inadequate capacity to dispose of sludge to sewer interruption. | [9 empty] | 0 | No
Slow Sand Filtration Risks | Deterioration of water quality due to cracking of media in filters | DWSP-T-037 | Microbiological contamination Turbidity Iron | Due to media disruption due to uneven flow or problems with under drainage. | [9 empty] | 0 | No
Slow Sand Filtration Risks | Deterioration of water quality due to cracking or failed underdrains | DWSP-T-038 | Microbiological contamination Turbidity Iron | Due to failed underdrains. | [9 empty] | 0 | No
Slow Sand Filtration Risks | Deterioration of water quality due to failure to mature filter before putting into use following cleaning | DWSP-T-039 | Microbiological Contamination Chemical contamination Turbidity | Due to lack of development of the schmutzdecke (biological layer) following cleaning. | Without the schmutzdecke the filter acts only as a sieve and is less efficient. Filter should be run to waste until turbidity is satisfactory. | [8 empty] | 0 | No
Slow Sand Filtration Risks | Deterioration of water quality due anaerobic conditions prevailing in filter. | DWSP-T-040 | Manganese Low oxygen levels | Due to anaerobic conditions releasing manganese | [9 empty] | 0 | No
Slow Sand Filtration Risks | Deterioration of water quality due to birds roosting on filters at night | DWSP-T-041 | Microbiological contamination | Due to bird roost due to large faecal loading | Bird excrement contains very large numbers of bacteria. | [8 empty] | 0 | No
Slow Sand Filtration Risks | Deterioration of water quality due to incorrect media being installed. | DWSP-T-042 | Microbiological contamination Turbidity | Due to use of wrong sand | Slow sand filtration requires angular sand rather than round sand. | [8 empty] | 0 | No
Slow Sand Filtration Risks | Inability to meet demand due to algal bloom | DWSP-T-043 | Loss of Supply | Due to block of filters due to large numbers of algal cells. | May also lead to unacceptable tastes and odours. | [8 empty] | 0 | No
Rapid Gravity Risks | Breakthrough of contaminants due to mud-balling in media. | DWSP-T-044 | Suspended solids Trace organics Residual coagulant Microbiological contamination | As a result of inadequate filtration due to state of filter due to inadequate washing. | May result from inadequate bed expansion or upflow rate failing to clean media. | [8 empty] | 0 | No
Rapid Gravity Risks | Breakthrough of contaminants as a result of filter wash plant failure | DWSP-T-045 | Suspended solids Trace organics Residual coagulant Microbiological contamination | Due to inadequate filtration due to overload of filter due to lack of washing. | If no standby available adequate spares should be carried. | [8 empty] | 0 | No
Rapid Gravity Risks | Breakthrough of contaminants as a result of inadequate frequency for backwash. | DWSP-T-046 | Suspended solids Trace organics Residual coagulant Microbiological contamination | Due to inadequate filtration due to overload of filter due to frequency of washing. | If allowed to operate in this way, the media may also become less efficient due to build up of dirt. | [8 empty] | 0 | No
Rapid Gravity Risks | Breakthrough of contaminants as a result of no slow start or run-to-waste following backwashing | DWSP-T-047 | Suspended solids Trace organics Residual coagulant Microbiological contamination | Due to inadequate filtration due to starting filter too quickly. | If filter is started at too high a rate before the bed has settled down filtration will be less efficient. | [8 empty] | 0 | No
Rapid Gravity Risks | Breakthrough of contaminants as a result of reduced capacity when one filter is out for backwash | DWSP-T-048 | Suspended solids Trace organics Residual coagulant Microbiological contamination | Due to inadequate filtration due to increased filter loading as a result of a filter being out of service for washing. | More likely if plant is running close to or exceeding its design capacity or is stressed due to poor raw water conditions. | [8 empty] | 0 | No
Rapid Gravity Risks | Breakthrough of contaminants as a result of uneven backwash | DWSP-T-049 | Suspended solids Trace organics Residual coagulant Microbiological contamination | Due to inadequate filtration due to uneven filter loading as a result of blocked filter nozzles. | The efficiency of some areas of the filter bed will be reduced, placing a greater load on areas that are OK. | [8 empty] | 0 | No
Rapid Gravity Risks | Breakthrough of contaminants as result of loss of media | DWSP-T-050 | Suspended solids Trace organics Residual coagulant Microbiological contamination | Due to inadequate filtration due to inadequate media depth. | Media loss may be greater in dual media filters. Anthracite/ carbon has a lower density and is washed over more easily | [8 empty] | 0 | No
Rapid Gravity Risks | Breakthrough of contaminants as result of failure to set correct coagulant or polyelectrolyte dose. | DWSP-T-051 | Suspended solids Trace organics Residual coagulant Microbiological contamination | As a result of floc that is too soft or too small penetrating the bed more rapidly. | A rise in treated water turbidity may indicate a problem. Flocculation tests should then be done to check floc formation. | [8 empty] | 0 | No
Rapid Gravity Risks | Breakthrough of contaminants as a result of wrong media in filter | DWSP-T-052 | Suspended solids Trace organics Residual coagulant Microbiological contamination | Due to inadequate filtration due to wrong grade of media. | If media is replaced ensure the right specification and check samples for effective size and uniformity coefficient to ensure that it is. | [8 empty] | 0 | No
Membrane Risks | Breakthrough of contaminants caused by dirty or damaged membrane | DWSP-T-053 | Suspended solids Trace organics Residual coagulant Microbiological contamination | As a result of inefficient cleaning of membranes due to failure of cleaning system | [9 empty] | 0 | No
Membrane Risks | Breakthrough of contaminants caused by dirty or damaged membrane | DWSP-T-054 | Suspended solids Trace organics Residual coagulant Microbiological contamination | As a result inadequate frequency of cleaning of membranes due to failure to follow operating procedures. | Important that all operators are adequately trained, | [8 empty] | 0 | No
Membrane Risks | Breakthrough of contaminants caused by dirty or damaged membrane | DWSP-T-055 | Suspended solids Trace organics Residual coagulant Microbiological contamination | Resulting from damage to membranes due to inadequate frequency of inspections or membrane integrity tests | Membrane integrity tests should be an integral part of the operation of membrane plants. | [8 empty] | 0 | No
Membrane Risks | Loss of supply due to CIP failure | DWSP-T-056 | Loss of Supply | Due to automatic plant shut-down | [9 empty] | 0 | No
Membrane Risks | Loss of supply due to 'deep clean' failure | DWSP-T-057 | Loss of Supply | Due to automatic plant shut-down | [9 empty] | 0 | No
Membrane Risks | Loss of supply due to integrity test failure | DWSP-T-058 | Loss of Supply | Due to manual plant shut-down | [9 empty] | 0 | No
Membrane Risks | Loss of supply due to particle count failure | DWSP-T-059 | Loss of Supply | Due to automatic plant shut-down | [9 empty] | 0 | No
Membrane Risks | Breakthrough of contaminants as a result of loss of membrane integrity. | DWSP-T-060 | Suspended solids Trace organics Residual coagulant Microbiological contamination | Due to membrane damage due to failure of pre-treatment. | [9 empty] | 0 | No
Membrane Risks | Deterioration of final water quality as a result of inability to dose coagulant | DWSP-T-061 | Chemical contamination | Due to decrease in membrane efficiency as a result of failure of coagulant dosing system. | [9 empty] | 0 | No
Membrane Risks | Inability to meet demand as a result of failure of backwash system | DWSP-T-062 | Loss of supply | Inability to operate membranes due to fouling due to inability to backwash membranes | [9 empty] | 0 | No
Membrane Risks | Inability to meet demand as a result of membrane feed pump failure | DWSP-T-063 | Loss of supply | Inability to operate membranes as a result of membrane feed pump failure. | If no standby available adequate spares should be carried. | [8 empty] | 0 | No
Disinfection Risks | Contamination of treated water as a result of accumulation of deposits in contact tank | DWSP-T-064 | Turbidity | As a result of carry over of sediment from contact tank. | [9 empty] | 0 | No
Disinfection Risks | Contamination of treated water as a result high bromate content of sodium hypochlorite | DWSP-T-065 | Chemical contamination | As a result of sodium hypochlorite not meeting supply specification | [9 empty] | 0 | No
Disinfection Risks | Contamination of treated water as a result of excessive formation of disinfection by-products | DWSP-T-066 | Chemical contamination | As a result of excessive disinfectant dose and high levels of trace organics | Due to formation of disinfection by-products | [8 empty] | 0 | No
Disinfection Risks | Inadequate treatment as a result of disinfection at wrong pH | DWSP-T-067 | Microbiological contamination | As a result of reduced disinfection efficiency due to pH out with optimum range | Disinfection efficiency is significantly affected by pH. | [8 empty] | 0 | No
Disinfection Risks | Failure of disinfection as a result of failure of chlorine gas flow | DWSP-T-068 | Microbiological contamination | Due to failure of disinfection due to failure of delivery system. | [9 empty] | 0 | No
Disinfection Risks | Failure of disinfection as a result of failure of UV | DWSP-T-069 | Microbiological contamination | Due to failure of disinfection due to failure of UV lamp. | [9 empty] | 0 | No
Disinfection Risks | Failure of disinfection as a result of failure of sodium hypochlorite delivery system. | DWSP-T-070 | Microbiological contamination | Due to failure of disinfection due to failure of delivery system. | [9 empty] | 0 | No
Disinfection Risks | Failure of disinfection as a result of failure or lack of automatic shutdown following disinfection process failure | DWSP-T-071 | Microbiological contamination | Due to WTW failing to shut down when disinfection fails. | [9 empty] | 0 | No
Disinfection Risks | Inadequate treatment as a result of reduced UV efficiency | DWSP-T-072 | Microbiological contamination | Due to reduction transmittance of light due to fouling of lamp sheath or to increase in colour or turbidity | If light transmission is reduced UV becomes less effective. | [8 empty] | 0 | No
Disinfection Risks | Inadequate treatment as a result of inability to meet disinfection requirements due to high chlorine demand | DWSP-T-073 | Microbiological contamination | Due to inability to add sufficient chlorine due to high flow or high chlorine demand | [9 empty] | 0 | No
Disinfection Risks | Inadequate treatment as a result of insufficient contact time | DWSP-T-074 | Microbiological contamination | Due to insufficient contact time to kill bacteria as a result of poor contact tank design or operating beyond design flow | [9 empty] | 0 | No
Disinfection Risks | Inadequate treatment as a result of incorrect chlorine dose | DWSP-T-075 | Microbiological contamination | Due to lack of residual controller and rapid change in chlorine demand, due to insufficient manual intervention. | [9 empty] | 0 | No
Disinfection Risks | Inadequate treatment as a result of failure of ammonia dosing system | DWSP-T-076 | Microbiological contamination Taste or odour | As a result of incorrect chlorine:ammonia ratio due to failure of ammonia dosing system | If using chloramination failure to reach the correct ratio of ammonia to chlorine affects disinfection. | [8 empty] | 0 | No
Disinfection Risks | Inadequate treatment due inadequate ventilation of hydrogen from OSEC unit | DWSP-T-077 | Explosion Loss of supply | As a result of build up of hydrogen as a result of inadequate ventilation. | [9 empty] | 0 | No
Ozone Risks | Inadequate Treatment due to low levels of ozone | DWSP-T-078 | Microbiological contamination | Due to failure to adequately reduce humidity of incoming air supply | [9 empty] | 0 | No
Ozone Risks | Inadequate Treatment due to high pH in water | DWSP-T-079 | Microbiological contamination | Due to rapid decay of ozone due to elevated pH in water | [9 empty] | 0 | No
Ozone Risks | Contamination of water due to excessive formation of ozonation by-products | DWSP-T-080 | Chemical contamination | As a result of high levels of pre-cursor organics in the incoming water | [9 empty] | 0 | No
Treated Storage Risks | Contamination of treated water as a result of vandalism | DWSP-T-081 | Microbiological contamination Chemical contamination | As a results of actions by intruders | As a minimum lids and air vents must be secure. Security fence may be needed if conditions warrant it. | [8 empty] | 0 | No
Treated Storage Risks | Contamination of treated water caused by rainwater ingress | DWSP-T-082 | Microbiological contamination Chemical contamination | As a result of lack of structural integrity of reservoir due to lack of inspection or maintenance | Reservoirs should be cleaned and inspected on a regular basis. | [8 empty] | 0 | No
Treated Storage Risks | Deterioration in water quality due to disturbance of sediment in reservoir | DWSP-T-083 | Microbiological contamination Turbidity Aluminium Iron | Due to disturbance of sediment on floor of reservoir due to low level and lack of maintenance. | Reservoirs should be cleaned and inspected on a regular basis. | [8 empty] | 0 | No
Treated Storage Risks | Loss of supply due to inadequate storage | DWSP-T-084 | Loss of supply | Due to insufficient storage to cope with fluctuations in demand. | Reservoirs may be undersized due to financial considerations. | [8 empty] | 0 | No
Facility Specific Risks |  | DWSP-T-200 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-T-201 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-T-202 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-T-203 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-T-204 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-T-205 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-T-206 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-T-207 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-T-208 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-T-209 | [11 empty] | 0 | No
M
S
>
<
REFORMAT ALL
INS

## Network Detail
Approval Holder
Water Supply System
Approval Number
Location
Network Information
Water Supply System
Length of Network
Mains Materials
Trunk Mains
Pumping Stations
Service Reservoirs and average residence times
Telemetry
Comments
M
>
<

## Network Schematic
Approval Holder
Water Supply System
Approval Number
Location
(Insert Schematic)
M
>
<

## Network Risks
Approval Holder
Water Supply System
Approval Number
Location
| Risk Description | Risk I.D. | Hazard | Cause of Potential Failure | Comment | Current Monitoring | How Risk is Currently Controlled | Assess if Control is Adequate | Do any Standard Procedures cover this | Likelihood | Consequence | L'Hood Score | Cons. Score | Risk Score | Key Risk | Required Interventions to Prevent Failure | Responsible Party
General Risks | Loss of supply from regional supply line | DWSP-N-001 | Loss of supply | Failure of flow from regional supply | [9 empty] | 0 | No |  |  | 1
General Risks | Build up of deposits in network as a result of inadequate flushing frequency and/or velocity | DWSP-N-002 | Discoloration Taste & Odour | Resulting from inadequate flushing of problem areas. | Areas where sediment is known to build up benefit from a regular flushing programme. | [8 empty] | 0 | No |  |  | 1
General Risks | Broken main as a result of PRV failure | DWSP-N-003 | Loss of supply Chemical contamination Microbiological contamination | As a result of a broken main due to high pressure due to failure of PRV. | PRVs should be serviced as required. | [8 empty] | 0 | No |  |  | 1
General Risks | Loss of supply and/or deterioration of water quality as a result of broken main | DWSP-N-004 | Loss of supply Chemical contamination Microbiological contamination | As a result of a broken main due to failure of pipe integrity. | May be as a result of many different circumstances | [8 empty] | 0 | No |  |  | 1
General Risks | Contamination of water as a result of cross-connection | DWSP-N-005 | Chemical contamination Microbiological contamination | As a result of connection with private supply due to customer having dual connection, no air gap | If customer has dual supply the pipework must be safely set up. | [8 empty] | 0 | No |  |  | 1
General Risks | Contamination of water due to leaking air valves | DWSP-N-006 | Chemical contamination Microbiological contamination | Resulting from ingress of water due to faulty air valve surrounded by water. | Air valves should be checked periodically. | [8 empty] | 0 | No |  |  | 1
General Risks | Contamination of water in supply as a result of the use of non-approved or inappropriate materials in the network | DWSP-N-007 | Chemical contamination | As a result of contact with inappropriate materials. | Any materials used in the network should comply with the appropriate standard. | [8 empty] | 0 | No |  |  | 1
General Risks | Contamination of water due to failure to follow proper hygiene practice when carrying out repairs. | DWSP-N-008 | Chemical contamination Microbiological contamination | Due to ingress of material from excavation and/or poor disinfection procedures. | Operators should be fully trained in proper hygiene practice | [8 empty] | 0 | No |  |  | 1
General Risks | Contamination of water in supply as a result of connection to mothballed or abandoned assets. | DWSP-N-009 | Chemical contamination microbiological contamination | As a result of connection to a main containing stagnant water. | All abandoned assets should be cut and capped rather than just valved off. | [8 empty] | 0 | No |  |  | 1
General Risks | Deterioration of water quality as a result of incorrect sequence of valve operations | DWSP-N-010 | Chemical contamination Microbiological contamination | As a result of flow reversal due to the need for rezoning due to the incorrect sequence of valve operations | Valves should be maintained and good records kept of their location and mode of operation, i.e. RH or LH thread. | [8 empty] | 0 | No |  |  | 1
General Risks | Deterioration of water quality in supply as a result of unauthorised connection to the network. | DWSP-N-011 | Chemical contamination | As a result of unauthorised connection to the network due to incorrect use of hydrants and standpipes. | Use of standpipes should be controlled to ensure that they have anti backflow devices and are used correctly. | [8 empty] | 0 | No |  |  | 1
General Risks | Deterioration of water quality due to change in normal flow pattern. | DWSP-N-012 | Chemical contamination | Due to mains sediment being disturbed by increased flow. | Iron, manganese, aluminium sediment | [8 empty] | 0 | No |  |  | 1
General Risks | Failure to meet demand as a result of failure to mend break in a reasonable time | DWSP-N-013 | Loss of supply | As a result of poor access. | [9 empty] | 0 | No |  |  | 1
General Risks | Failure to meet demand due to inability to operate valves as required. | DWSP-N-014 | Loss of supply | Inability to operate valves when needed due to the lack of maintenance | If valves are not operated and checked they may become difficult to operate. | [8 empty] | 0 | No |  |  | 1
General Risks | Failure to meet demand as a result of insufficient valves to isolate area affected by break | DWSP-N-015 | Loss of supply | Due to high loss of water due lack of isolation of mains | [9 empty] | 0 | No |  |  | 1
General Risks | Failure to meet demand as a results of operating system above design pressure | DWSP-N-016 | Loss of supply | Due to broken mains as a result of operating mains above design pressure. | [9 empty] | 0 | No |  |  | 1
General Risks | Failure to meet demand as a result of failure of pipe bridge | DWSP-N-017 | Loss of supply | As a result of mains break due to pipe bridge collapse. | Pipe bridge structures should be checked regularly. | [8 empty] | 0 | No |  |  | 1
General Risks | Failure to meet demand as a result of breakss caused by age-related deterioration. | DWSP-N-018 | Loss of supply | Resulting from break due to deterioration of pipe condition due to age. | Planned maintenance/renewal should prevent this problem occurring. | [8 empty] | 0 | No |  |  | 1
General Risks | Iron discoloration in water as a result of metal pick-up from the mains material. | DWSP-N-019 | Chemical contamination | Resulting from mains corrosion due to mains material and prevailing water quality. | Older pipe materials in use may not comply with current standards. May also be affected by flow rate. | [8 empty] | 0 | No |  |  | 1
General Risks | Loss of pressure as a result of leakage | DWSP-N-020 | Loss of supply Loss of pressure | Due to leakage due to inadequate leakage control/poor maintenance. | If system leakage rates are high, a leakage control programme is recommended. | [8 empty] | 0 | No |  |  | 1
General Risks | Loss of supply or pressure or contamination of water in supply as a result of fire service tackling a fire | DWSP-N-021 | Loss of supply Loss of pressure Microbiological contamination Chemical contamination | Due to high flow rate or changes in flow patterns, or loss of disinfectant contact time or disturbance of sediment | [9 empty] | 0 | No |  |  | 1
General Risks | Loss of supply or contamination of water in supply as a result of excessive demand in a short period of time | DWSP-N-022 | Loss of supply Chemical contamination | Lack of communication from external stakeholders, e.g. builders, fire service | Fire service should be aware that if they are testing hydrants they should notify water operators. | [8 empty] | 0 | No |  |  | 1
General Risks | Loss of supply as a result of failure of critical main due to lack of alternative supply | DWSP-N-023 | Loss of supply | Due to break on a critical main such that no alternative means of supply is available | [9 empty] | 0 | No |  |  | 1
General Risks | Microbiological growth in distribution system as a result of oversized mains | DWSP-N-024 | Microbiological contamination | Build up of biofilms in the network due to excessive dwell time as a result of incorrectly sized mains. | Biofilms are more likely to develop in areas of low flow where disinfectant residual may be very low. | [8 empty] | 0 | No |  |  | 1
General Risks | Microbiological growth in distribution system as a result of low disinfectant residual | DWSP-N-025 | Microbiological contamination | Build up of biofilms in the network due to inadequate residual disinfectant. | [9 empty] | 0 | No |  |  | 1
General Risks | Migration of hydrocarbons and other contaminants through pipework as a result of inappropriate materials used in areas of contaminated land | DWSP-N-026 | Chemical contamination | Resulting from use of inappropriate materials in areas of contaminated land | All polyethylene pipes are susceptible to migration of hydrocarbons through the pipe wall. | [8 empty] | 0 | No |  |  | 1
General Risks | Health risk to vulnerable customer due to inability to operate dialysis machine or similar | DWSP-N-027 | Loss of supply | Due to loss of supply | [9 empty] | 0 | No |  |  | 1
General Risks | Pressure problems caused by PRV failure | DWSP-N-028 | Loss of pressure High pressure | Pressure fluctuation due to the failure of PRV. | PRVs should be serviced as required. | [8 empty] | 0 | No |  |  | 1
Pumping Station Risks | Failure of pump control panel resulting in power loss | DWSP-N-029 | Loss of supply | As a results of inability to operate pumps due to lack of power | [9 empty] | 0 | No |  |  | 1
Pumping Station Risks | Failure of pumps due to breakdown and no standby | DWSP-N-030 | Loss of supply | As a result of mechanical breakdown and lack of standby pump. | [9 empty] | 0 | No |  |  | 1
Pumping Station Risks | Oil contaminating water due to use of unacceptable pump lubricants. | DWSP-N-031 | Hydrocarbon contamination | Due to non food grade leaking into wet well. | All pumps should use food grade lubricants. | [8 empty] | 0 | No |  |  | 1
Pumping Station Risks | Failure of pumps due to power surge at pump station. | DWSP-N-032 | Loss of supply | Due to pump failure due to electrical fault caused by power surge. | If electrical supply is subject to power fluctuations surge protection should be used. | [8 empty] | 0 | No |  |  | 1
Pumping Station Risks | Failure of pumps due to flooding | DWSP-N-033 | Loss of supply | Due to inadequate drainage or poor siting of pump house | [9 empty] | 0 | No |  |  | 1
Pumping Station Risks | Failure to meet demand as a result of loss of power supply | DWSP-N-034 | Loss of supply | Due to power failure and no standby generator. | [9 empty] | 0 | No |  |  | 1
Pumping Station Risks | Failure to meet demand due to insufficient pumping capacity | DWSP-N-035 | Loss of supply Low pressure | Due to pumps operating below rating or inadequately sized. | Pump capacity should be matched to expected demand. | [8 empty] | 0 | No |  |  | 1
Reservoir Risks | Contamination of water as a result of sediment deposition in reservoir | DWSP-N-036 | Chemical contamination Microbiological contamination. | Due to build up of sediment in bottom of reservoir as a result of inadequate maintenance. | Reservoirs should be emptied, inspected and cleaned on a regular basis. | [8 empty] | 0 | No |  |  | 1
Reservoir Risks | Contamination of water due to ingress of water as a result of inadequate structure or maintenance. | DWSP-N-037 | Chemical contamination Microbiological contamination. | Due to lack of structural integrity of reservoir as a result of poor design or maintenance | Common weaknesses are lids, ducting holes for cables, poorly sealed roof joints, air vents. | [8 empty] | 0 | No |  |  | 1
Reservoir Risks | Contamination of water due to ingress of organic debris as a result of inadequate structure or maintenance. | DWSP-N-038 | Chemical contamination Microbiological contamination. | Due to lack of structural integrity of reservoir as a result of poor design or maintenance | More of a problem on earth covered reservoirs where plant roots may penetrate structure. | [8 empty] | 0 | No |  |  | 1
Reservoir Risks | Contamination of water due to poor hygiene practice when doing planned inspection or maintenance. | DWSP-N-039 | Chemical contamination Microbiological contamination. | Due to poor hygiene practice or use of non-approved chemicals. | Operators should be fully trained in proper hygiene practice | [8 empty] | 0 | No |  |  | 1
Reservoir Risks | Contamination of water due to reservoir running empty due to faulty or no telemetry. | DWSP-N-040 | Chemical contamination | Due to disturbance of sediment on floor of reservoir due to low level as a result of lack of alarm. | Regular cleaning will help keep sediment build up to a minimum. | [8 empty] | 0 | No |  |  | 1
Reservoir Risks | Contamination of water as a result of vandalism | DWSP-N-041 | Chemical contamination Microbiological contamination. | Due to vandalism, due to lack of secure fencing and structure. | Degree of security required will depend on location. | [8 empty] | 0 | No |  |  | 1
Reservoir Risks | Contamination of water due to access to reservoir by stock or wildlife | DWSP-N-042 | Microbiological contamination | Due to lack of secure fencing round reservoir. | [9 empty] | 0 | No |  |  | 1
Reservoir Risks | Contamination of water due vermin accessing reservoir | DWSP-N-043 | Microbiological contamination | Due to lack of mesh or flap valve on overflow from reservoir. | [9 empty] | 0 | No |  |  | 1
Reservoir Risks | Deterioration of water quality due to thermal stratification | DWSP-N-044 | Chemical contamination Microbiological contamination. | Due to hot weather and reservoir being above ground and inadequately insulated and poor circulation | [9 empty] | 0 | No |  |  | 1
Reservoir Risks | Deterioration of water quality due to poor circulation in reservoir | DWSP-N-045 | Chemical contamination | Due to poor design of reservoir | Design should encourage circulation. | [8 empty] | 0 | No |  |  | 1
Reservoir Risks | Deterioration of water quality due to excessive residence time of water in reservoir. | DWSP-N-046 | Chemical contamination Microbiological contamination. | Due to long storage time in reservoir and likely loss of disinfectant residual. | [9 empty] | 0 | No |  |  | 1
Reservoir Risks | Failure to meet demand as a result of reservoir being undersized | DWSP-N-047 | Loss of supply | Due to inability to allow sufficient throughput. | If reservoir is often running low it is also likely to entrain air. | [8 empty] | 0 | No |  |  | 1
Reservoir Risks | Failure to meet demand as a result of inability to access reservoir to correct fault | DWSP-N-048 | Loss of supply | Due to poor weather making access impossible. | [9 empty] | 0 | No |  |  | 1
Facility Specific Risks |  | DWSP-N-300 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-N-301 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-N-302 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-N-303 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-N-304 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-N-305 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-N-306 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-N-307 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-N-308 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-N-309 | [11 empty] | 0 | No
M
S
>
<
REFORMAT ALL
INS

## Customer Detail
Approval Holder
Water Supply System
Approval Number
Location
Customer Information
Water Supply System
Are By-Laws in Place?
Are there compliance checks?
Population Supplied
No. of Domestic Properties
No. of Business Properties
Hospitals
Other Medical Premises
Dialysis Patients
Prisons etc.
Schools
Care Homes
Is plumbosolvency an issue?
Comments
M
>
<

## Customer Risks
Approval Holder
Water Supply System
Approval Number
Location
| Risk Description | Risk I.D. | Hazard | Cause of Potential Failure | Comments | Current Monitoring | How Risk is Currently Controlled | Assess if Control is Adequate | Do any Standard Procedures cover this | Likelihood | Consequence | L'Hood Score | Cons. Score | Risk Score | Key Risk | Required Interventions to Prevent Failure | Responsible Party
General Risks | Lead in water in supply picked up from the service pipes and other fittings | DWSP-C-001 | Chemical contamination | Resulting from dissolved lead from internal pipework or lead solder. | [9 empty] | 0 | No
General Risks | Contamination of water in supply due to reduction in disinfectant levels resulting from long residence time of water in pipe caused by incorrectly sized/long service pipe. | DWSP-C-002 | Chemical contamination Microbiological contamination | Disinfectant decay due to long residence time of water in pipe due to long service pipe | Service may have been installed without any consideration of residence time in service pipe | [8 empty] | 0 | No
General Risks | Contamination of water in supply as a result of chloramine decay and production of nitrites | DWSP-C-003 | Chemical contamination Microbiological contamination | As a result of long residence time in network creating chloramine decay and formation of high levels of nitrite | [9 empty] | 0 | No
General Risks | Contamination of water in supply or pressure problems as a result of leaking service pipe | DWSP-C-004 | Microbiological contamination Loss of pressure | Due to ingress due to leaking service pipe | If a leaking service pipe is sitting in water and there is a sudden drop in pressure, water may drawn in. | [8 empty] | 0 | No
General Risks | Contamination of water in supply as a result of unsatisfactory or damaged new connections caused by inadequate installation procedures. | DWSP-C-005 | Chemical contamination Microbiological contamination | As a result of unsatisfactory or damaged new connections due to bad installation and failure to follow a suitable code of practice | If the pipe ends are not protected during installation then swarf or dirt may enter the pipe and cause contamination. | [8 empty] | 0 | No
General Risks | Hydrocarbon contamination as a result of laying service in contaminated land. | DWSP-C-006 | Chemical contamination. | As a result of fuel/oil leak in soil through which polyethylene pipe is laid. | Hydrocarbons can migrate through polyethylene pipe. | [8 empty] | 0 | No
General Risks | Contamination of water in supply as a result of connection to unwholesome water due to lack of knowledge/supervision. | DWSP-C-007 | Chemical contamination Microbiological contamination | Due to incorrect connection to unwholesome water due to lack of knowledge/supervision | Use of non-certified tradesmen may lead to unsatisfactory conditions | [8 empty] | 0 | No
General Risks | Contamination of water in supply as a result of use of inappropriate material in the presence of contaminated land | DWSP-C-008 | Chemical contamination. | Due to the use of inappropriate material due to the presence of contaminated land. | If laying pipes in contaminated land, contractors must install appropriate pipe materials. | [8 empty] | 0 | No
General Risks | Contamination of water in supply as a result of back siphonage caused by the lack of appropriate backflow protection | DWSP-C-009 | Chemical contamination Microbiological contamination | Resulting from back siphonage due to the lack of appropriate backflow protection, i.e. non-return valve. | Industrial/Commercial Premises are generally High Risk; Household Customers are generally Low Risk, although preparing pesticides for garden use potentially high. | [8 empty] | 0 | No
General Risks | Pressure problems as a result of leakage caused by corrosion | DWSP-C-010 | Loss of pressure | Resulting from leakage due to corrosion of copper pipework due to lack of protection or maintenance | Pitting corrosion or electrolytic or galvanic corrosion may cause leakage or failure. | [8 empty] | 0 | No
General Risks | Increased water temperature as a result of inadequate design of storage facility or internal pipework | DWSP-C-011 | Chemical contamination Microbiological contamination | Warm water due to on site storage above required temp due to inappropriate storage facility/lack of insulation | Elevated temperature may encourage microbial growth. | [8 empty] | 0 | No
General Risks | Contamination of water in supply as a result of loss of chlorine residual caused by increased temperature | DWSP-C-012 | Microbiological contamination | Resulting from loss of chlorine residual due to increase in temperature. | May give rise to microbial growth. | [8 empty] | 0 | No
General Risks | Contamination of water in supply as a result of inappropriate plumbing | DWSP-C-013 | Chemical contamination Microbiological contamination | Resulting from use of inappropriate plumbing materials | Plumbers should only use materials approved for potable water. | [8 empty] | 0 | No
General Risks | Contamination of water in supply as a result of open storage cistern with no lid. | DWSP-C-014 | Chemical contamination Microbiological contamination | Due to open storage tank due to inadequate plumbing work. | Open storage tanks may attract birds or other animals that may drown. Dust may be a problem too. | [8 empty] | 0 | No
General Risks | Contamination of water in supply as a result of the situation of the storage tank or lack of maintenance. | DWSP-C-015 | Microbiological contamination | Resulting from poor condition of on site storage tanks due to lack of inspection/maintenance. | Inside of Tank needs to be inspected and cleaned Should be situated away from direct sunlight and insulated to keep cool. | [8 empty] | 0 | No
General Risks | Contamination of water in supply as a result of installation of inappropriate appliances | DWSP-C-016 | Microbiological contamination | Resulting from installation of inappropriate water filters and cartridges. | Any point of use device should be approved for potable water use. | [8 empty] | 0 | No
General Risks | Contamination of water in supply caused by bacterial growth in appliances as a result of inadequate maintenance | DWSP-C-017 | Microbiological contamination | Due to growth of bacteria in water filters or cartridges resulting from inadequate maintenance. | If cartridges or filters are not changed regularly internal bacterial growth may occur. | [8 empty] | 0 | No
General Risks | Contamination of water in supply as a result of use of drip feed cisterns | DWSP-C-018 | Chemical contamination Microbiological contamination | As a result of ingress of contamination due to failure to operate proper hygiene practice. | [9 empty] | 0 | No
General Risks | Contamination of water in supply as a result of cisterns being supplied from tankers | DWSP-C-019 | Microbiological contamination | As a result of ingress of contamination due to failure to operate proper hygiene practice. | [9 empty] | 0 | No
General Risks | Contamination of water in supply as a result of inadequate hygiene practice at bulk water filling stations | DWSP-C-020 | Chemical contamination Microbiological contamination | As a result of ingress of contamination due to failure to operate proper hygiene practice. | If hoses are not properly managed and kept from coming into contact with the ground or other undesirable material contamination can easily occur. | [8 empty] | 0 | No
Facility Specific Risks |  | DWSP-C-400 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-C-401 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-C-402 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-C-403 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-C-404 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-C-405 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-C-406 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-C-407 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-C-408 | [11 empty] | 0 | No
Facility Specific Risks |  | DWSP-C-409 | [11 empty] | 0 | No
M
S
>
<
REFORMAT ALL
INS

## Key Risks
Approval Holder
Water Supply System
Approval Number
Location
Last run: January-23-2012 13:27
| Risk Description | Risk I.D. | Hazard | Cause of Potential Failure | Comments | Current Monitoring | How Risk is Currently Controlled | Assess if Control is Adequate | Do any Standard Procedures cover this | Likelihood | Consequence | L'Hood Score | Cons. Score | Risk Score | Key Risk | Required Interventions to Prevent Failure | Responsible Party
[14 empty] | 0 | No
M
S
CLEAR THEN
CONSOLIDATE RISKS

## Action Summary
Approval Holder
Water Supply System
Approval Number
Location
Summary of Actions Required to Mitigate the Main Risks identified
| Risk Description | Risk ID | Possible Additional Short Term Controls | Intervention (s) Identified | Is There Funding? | Person Responsible | Expected Start Date | Expected Finish Date | Comments
M
S
UPDATE
ACTION SUMMARY

## SOPs
Approval Holder
Water Supply System
Approval Number
Location
Standard Operating Procedures
List here all operating procedures that apply to the operation of your water supply system
Identifying Code or Number | Description
M